## Sheet1
S. | Category | Marks weightage | Max marks
No.
1 | The proposed Data center should be certified for | 0.5 mark for each certification | 5
· ISO 9001
| · ISO 27001 | 5 marks for all the certifications
· ISO 22301
· ISO 20000-1
· ISO 45001
· ISO 50001
· ISO 14001
· PCI DSS
· SOC 1
· SOC 2
2 | The bidder must be the owner of the proposed Data Center services provided to BOBCARD or in case of leased Land, an unexpired lease period must be minimum 35 years | 2 marks for <35 years | 3
3 marks for above >35 years
3 | Age of the Building should not be more than 15 years old. It should be complied with all observations for structural audit conducted in last 3 years | 1 mark for more than =15 years | 3
2 marks for less than = 15 years
3 marks for less than = 10 years
4 | The Data Center should have a load bearing capacity of 1500 Kg/Sqmtr. | 1 mark for <1500 Kg/Sqmtr. | 2
2 marks for >=1500 Kg/Sqmtr.
5 | The Server Room Area should have raised floor height of minimum 1.5 ft. | 0.5 mark for raised floor height 1.5 ft | 1
0.75 mark for raised floor height above 1.5 - 2 ft
1 mark for above raised floor height above 2 ft
6 | The server hall height from raised floor to false ceiling should be at least 9.0 ft. | 1 mark for server hall height =< 9.0 ft | 2
2 marks for server hall height above 9 ft
7 | If proposed Co located site’s uptime on monthly basis is between 99.982% and 99.995% both inclusive | 2 marks if 99.982 to 99.995 | 3
3 marks if above 99.995
8 | The proposed data centre floor should be covered under comprehensive insurance on ongoing basis including risk related to earthquake, floods, fire, lightening, terrorist attacks etc. |  | 1
9 | Diesel Tanks (for generators) –It should have high capacity diesel tanks for ensuring minimum 48 hour power backup with contracts for fuel supply on demand. Copy of License from explosives department to store the diesel should be shared with bank. | 2 Mark if <48 hours | 3
3 Marks if > =48 hours
10 | Generators should be available in minimum N+1 redundancy | 2 marks if N+1 redundancy is configured | 3
3 marks if above N+2 or N+N redundancy is configured
11 | Two independent power suppliers/ substations / Transformer/RMU Level redundancy each capable of supporting the site independently should be available. | 2 mark if only redundancy at Transformer level | 4
3 marks if redundancy at RMU level & Transformer level
4 marks if redundancy at Substation & RMU & Transformer level
12 | UPS should be configured in N+1 redundancy mode for each source of power supply | 1 mark if N+1 redundancy is configured | 3
2 marks if N+2 redundancy is
configured
3 marks if N+3 or N+N redundancy is configured
13 | Data Center should maintain the PUE Maximum 1.7 | 1 mark for 1.65-1.7 | 2
2 mark for below 1.65
14 | Chiller/ Precision ACs specifications should be minimum of N+1 redundancy level | 1 mark if having Air Cooled based ACs with N+1 redundancy | 3
2 mark if having Water Cooled based ACs with N+1 redundancy
3 mark if having Either water Cooled or air cooled with N+2 & above, N+N redundancy level
15 | The temperature in the server hall should be maintained at 22 +/- 2 °C |  | 1
16 | The humidity at the Data Center should be maintained at 50 % +/- 5% RH |  | 1
17 | Fire Protection specification should have VESDA & NN 100, FM200/FE 227 Gas Suppression System, NOVEC 1230, Double Interlock Type Pre-Action Sprinkler System outside cage area. | 2 marks if NOVEC 1230 | 2
1 mark if FM 200
18 | Comprehensive Power Audit in the last two years / Record of past incidents should be available for the site/campus | 1 mark if only audit report of latest i.e. last one year is available | 2
2 marks if two years available
19 | Should have co-location business for atleast 5 customers of commercial banks/NBFC/ BFSI/commercial entities | 1 mark for hosting the each commercial bank in the proposed site.(Max. 5 counted for marks) 0.5 mark for hosting the Insurance/MF/NBFC in the proposed site. (Max. 5 counted for marks) 0.25 mark for hosting the commercial entities in the proposed site.(Max. 5 counted for marks) | 5
20 | Should have partner connect link to public cloud service provider | 0.5 mark for connectivity with one public cloud provider .75 mark for connectivity with two public cloud provider 1 mark for connectivity with three public cloud provider | 1
Total |  |  | 50